## BaseSheet (hidden)
DO NOT DELETE THIS SHEET
On
Off
On-Off
Off-On
Sequential
Stochastic single-pole
Stochastic 3-pole
None
Yes
No
GFortran 4.2.1
GFortran 4.6.2
Intel 16.0.110
Intel 16.0.110 (64-bit)
Intel 16.0.207
Intel 16.0.207 (64-bit)

## Input_Data
Study type | Value | Units | Comment | Select the type of study done in PSCAD
Jump to Post Processing | No | str | If you say Yes only the post processing is done. You need to already have the PSCAD results in this case
Frequency Sweep | No | str | If you say Yes to that the script ignores all that is not the sweep
Switch operation | Off | str | Select the type of switching for the breaker in the study
Switch type | Sequential | str | Sequential or Stochastic
Faults | No | str | Are there faults in your study? Yes or No - Faults are only applicable in sequential studies
Residual Flux | No | str | Consider residual flux of transformers? Yes or No - Only for TX Energisation studies
Set Up - Which folders, libraries, files do you need in the Case_folder?
Parameter | Value | Comment
Folders |  | Put the folder names that you need separated by commas. The folders must be in the root folder
Libraries |  | Relative paths to library names that you need separated by commas. The libs must be in the root folder - Use "Foldername\" if inside folder
Files inside cases |  | Relative paths to file names that you need separated by commas. The folders containing them must be in the root folder - Use "Foldername\" if inside folder
Files in Case_folder |  | Relative paths to file names that you need separated by commas. The files must be in the root folder - Use "Foldername\" if inside folder
Input parameters pre Snapshot
Parameter | Value | Units | Comment | These base parameters will be used for all the studies
Frequency | 60 | Hz | Grid frequency
Initialisation duration | 2.01 | s | Total run time of simulation
Time step | 2 | us | Simulation time step. Recommended 2 for SFO and 5 for TOV
Plot step | 20 | us | Simulation plot step. Recommended 20 for SFO and 100 for TOV
Create cases | Yes | str | Think carefully before changing this - This will jump the case creation and jump straigth to run snapshot, then run simulations
Take Snapshot | Yes | str | Think carefully before changing this - You NEED a Snapshot to run studies this option is only applicable when you already have a snapshot (exception to Freq Sweep) - Choose No if you already have the snapshots from a previous run - If you have a client file think thrice
Adjust names | No | str | If you switch to No, the MMs, CBs, ZMs, and TOVs names and will not be adjusted by script. It will make case creation faster but more prone to human error
Snapshot Time | 2 | Real | Snapshot time as a real number, only works when snap_shot > 0
Client file exist | No | str | This option enable 1 model for MPE and 1 for client. Typical of Orsted studies to not provide MPE IP
MPE Workspace | Formosa_IV.pswx | str | Name of .pswx file for internal MPE use
Client Workspace |  | str | Name of .pswx file that can be sent to client
FORTRAN Compiler | Intel 16.0.207 | str | Extension of FORTRAN genrated folder
Parallel simulations | 3 | Int | Number of simulations to be run in parallel
PSCAD instances | 4 | Int | Number of simulations to be run in parallel
Set Up - Define the auto controllers you want to use?
Parameter | Value | Comment |  | These are the variables in the client PSCAD file
Auto_Ctrl |  | List | If Client file exists select the controlled variables in the order they appear
Input parameters post Snapshot
Parameter | Value | Units | Comment | These parameters will be used for all the studies
Final duration | 1 | s | Total run time of simulation after snapshot
Parameters for fault (Sequential runs)
Parameter | Value | Units | Comment | Use faults with some switching (defines the switch stop). If you desire no switching don`t use SWITCH in Comp_Stat
Fault start | 1.1 | Real | Start of Range for Fault
Fault increment | 0.0016667 | Real | Increment for each run in s [Inc1R] - That is only relevant if Switch type is None then the multirun is only defined by faults
Fault end | 1.1317 | Real | End of Range for fault - That is only relevant if Switch type is None then the multirun is only defined by faults
Parameters for multiple run component (Sequential mrun component)
Parameter | Value | Units | Comment | These parameters will be used for sequential switching
Switch start | 2.2 | Real | If you have faults pay attention to Fault starts (Should be greater than switch start)
Switch increment | 0.0016667 | Real | If you have faults pay attention to Fault starts (Should be the same unless special conditions apply)
Switch stop | 2.215 | Real | End of Range for Variable 1 in s [Max1R]
2nd Switch delay | 0.1 | Real | Time delay to perform 2nd switch after 1st switch
Parameters for multiple run component (Stochastic mrun component)
Parameter | Value | Units | Comment | These parameters will be only used for stochastic switching
N1R | 5 | Int | Number of Runs for Variable 1
N2R | 5 | Int | Number of Runs for Variable 2
N3R | 4 | Int | Number of Runs for Variable 3
Min1R | 2.05 | Real | Start of Range for Variable 1 (Switching on one cylcle, 20ms for 50Hz)
Max1R | 2.0667 | Real | End of Range for Variable 1
Min2R | -0.003 | Real | Start of Range for Variable 2 - Breaker scatter if 3-pole switching selected or start of range if single-pole switching selected
Max2R | 0.003 | Real | End of Range for Variable 2 - Breaker scatter if 3-pole switching selected or end of range if single-pole switching selected
Min3R | -0.003 | Real | Start of Range for Variable 3 - Breaker scatter if 3-pole switching selected or start of range if single-pole switching selected
Max3R | 0.003 | Real | End of Range for Variable 3 - Breaker scatter if 3-pole switching selected or end of range if single-pole switching selected
Frequency sweep options
Parameter | Value | Units | Comment | These parameters will be used for Frequency Sweep. It is recommended to have client file when doing Frequency Sweep so that the taps you use are the correct ones for your study
Min Frequency | 0 | Hz | Min frequency for sweep (Fmin)
Max Frequency | 360 | Hz | Min frequency for sweep (Fmax)
Frequency increment | 2 | Hz | Steps of frequency increment (Finc)
Increment Type | 0 | Int | Linear = 0, log = 1 (FType)
Z output type | 0 | Int | Sequence impedance = 0, Phase impedance =1 (HType)
Frequency units | 0 | Hz | Frequency output units (FUnits)
Impedancce output units | 1 | Int | Magnitude and phase =0, real and imaginary = 1 (HUnits)
Post Process
Parameter | Value | Units | Comment
Number of cores | Auto | - | Number of cores to be used in the Post Processing. Auto will use 90% of PC capacity limited to 60 cores (Python limit)
The values in grey should only be modified if required for studies otherwise kept as default

## Comp_Stat
Breaker_Status
Definition | Breaker | C22_S1_TT9_TC9_L | C22_S2_TT9_TC9_F | C22_S3_TT9_TC9_L | C21_S1_TT6_TC1_F | C21_S1_TT9_TC5_F | C21_S1_TT9_TC9_F | C21_S2_TT9_TC5_F | C21_S3_TT9_TC9_F | C23_S1_TT9_TC8_L | C23_S1_TT9_TC9_L | C23_S3_TT1_TC1_L | C23_S3_TT2_TC1_F
CB_161_FIC | CB | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH | SWITCH
CB_161_TPC | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_161_ONS | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_161_ONT1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_161_ONT2 | CB | ON | ON | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_22_ONT1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_22_ONT2 | CB | ON | ON | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_22_TIE | CB | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
CB_230_ONT1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_230_ONT2 | CB | ON | ON | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_230_TIE | CB | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_230_ONC1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_230_ONC2 | CB | ON | ON | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_230_VSR1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | OFF | OFF | OFF | OFF
CB_230_VSR2 | CB | ON | ON | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_230_HF1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | OFF | OFF | OFF | OFF
CB_230_HF2 | CB | ON | ON | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | ON
CB_230_OFT1 | CB | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON | ON
CB_230_OFT2 | CB | ON | OFF | ON | OFF | OFF | OFF | OFF | OFF | ON | ON | ON | OFF
CB_66_OFT1 | CB | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
CB_66_OFT2 | CB | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
CB_66_TIE | CB | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF | OFF
Fault_level
Main | Script_FL | 0.4516 | 0.3218 | 0.1921 | 0.4516 | 0.4516 | 0.4516 | 0.3218 | 0.1921 | 0.4516 | 0.4516 | 0.1921 | 0.1921
Main | Script_FL | 5.3871 | 3.7121 | 2.0371 | 5.3871 | 5.3871 | 5.3871 | 3.7121 | 2.0371 | 5.3871 | 5.3871 | 2.0371 | 2.0371
Main | Script_FL | 0.8929 | 0.5677 | 0.2425 | 0.8929 | 0.8929 | 0.8929 | 0.5677 | 0.2425 | 0.8929 | 0.8929 | 0.2425 | 0.2425
Main | Script_FL | 9.0988 | 5.5656 | 2.0324 | 9.0988 | 9.0988 | 9.0988 | 5.5656 | 2.0324 | 9.0988 | 9.0988 | 2.0324 | 2.0324
Constants
Main | AC_Vgridpu | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Main | ONT_Z | 0.154 | 0.154 | 0.154 | 0.1435 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154 | 0.126 | 0.1295
OnSS_VSR1 | I_VSR | 0.585 | 0.585 | 0.585 | 0.531 | 0.557 | 0.585 | 0.557 | 0.585 | 0.678 | 0.678 | 0.678 | 0.678
OnSS_VSR2 | I_VSR | 0.585 | 0.585 | 0.585 | 0.531 | 0.557 | 0.585 | 0.557 | 0.585 | 0.678 | 0.678 | 0.678 | 0.678
Note on B26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: R+
Note on B27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: X+
Note on B28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: R0
Note on B29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: X0

## Layer_Stat
Layers
Layer | String | C22_S1_TT9_TC9_L | C22_S2_TT9_TC9_F | C22_S3_TT9_TC9_L | C21_S1_TT6_TC1_F | C21_S1_TT9_TC5_F | C21_S1_TT9_TC9_F | C21_S2_TT9_TC5_F | C21_S3_TT9_TC9_F | C23_S1_TT9_TC8_L | C23_S1_TT9_TC9_L | C23_S3_TT1_TC1_L | C23_S3_TT2_TC1_F
Extra | TC1 | Disable | Disable | Disable | Enable | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Enable
Extra | TC2 | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable
Extra | TC3 | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable
Extra | TC4 | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable
Extra | TC5 | Disable | Disable | Disable | Disable | Enable | Disable | Enable | Disable | Disable | Disable | Disable | Disable
Extra | TC6 | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable
Extra | TC7 | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable
Extra | TC8 | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Enable | Disable | Disable | Disable
Extra | TC9 | Enable | Enable | Enable | Disable | Disable | Enable | Disable | Enable | Disable | Enable | Disable | Disable
Sweep_Components
Main | FS_OSS | Disable | Enable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable | Disable

## Res_Flux
R_flux
Layer | Trf | C22_S1_TT9_TC9_L | C22_S2_TT9_TC9_F | C22_S3_TT9_TC9_L | C21_S1_TT6_TC1_F | C21_S1_TT9_TC5_F | C21_S1_TT9_TC9_F | C21_S2_TT9_TC5_F | C21_S3_TT9_TC9_F | C23_S1_TT9_TC8_L | C23_S1_TT9_TC9_L | C23_S3_TT1_TC1_L | C23_S3_TT2_TC1_F
Main | OSS_TX1 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4
Main | OSS_TX2 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4 | 0.8,-0.4,-0.4

## MM_blocks
Group | Un | Um | SDPF_LG | SDPF_LL | SIWL_LG | SIWL_LL | LIWL
MM_161_TPC | 161 | 170 | 325 | 325 | 620 | 620 | 750
MM_161_ONS | 161 | 170 | 325 | 325 | 620 | 620 | 750
MM_161_ONT1 | 161 | 170 | 325 | 325 | 620 | 620 | 750
MM_161_ONT2 | 161 | 170 | 325 | 325 | 620 | 620 | 750
MM_22_ONS1 | 22.8 | 24 | 50 | 50 | 116 | 116 | 145
MM_22_ONS2 | 22.8 | 24 | 50 | 50 | 116 | 116 | 145
MM_22_ONT1 | 22.8 | 24 | 50 | 50 | 116 | 116 | 145
MM_22_ONT2 | 22.8 | 24 | 50 | 50 | 116 | 116 | 145
MM_230_ONS1 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_ONS2 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_ONT1 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_ONT2 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_ONC1 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_ONC2 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_VSR1 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_VSR2 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_OSS1 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_OSS2 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_OFT1 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_230_OFT2 | 230 | 245 | 460 | 460 | 850 | 850 | 1050
MM_66_OFT1 | 66 | 72.5 | 140 | 140 | 260 | 260 | 325
MM_66_OFT2 | 66 | 72.5 | 140 | 140 | 260 | 260 | 325
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Calculated with FP
Note on F22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Calculated with FP